## Asset Table
BMS ASSET REGISTER — Building A (DesigoCC) & Building B (Niagara Tridium)
Site: Same Location · Shared: Roof Chiller Plant · Prepared by: Imami Joel Betofe · June 2026
Asset ID | Asset Name | Type | Building | Floor(s) | Function | Key Components / Sensors | Communicates With | Failure Impact | Status
AHU-A-GF-01~05 | Air Handling Units (x5) | AHU | Building A | Ground | Condition and distribute air to the floor via VAVs and FCUs; request heating/cooling from chiller plant | VSD fan, chilled water valve, filters, heating interlock, supply/return air temp sensors, static pressure sensor, CHW supply/return temp sensors, time clock | Chiller plant, VAVs, FCUs, DesigoCC | Loss of conditioned air to entire ground floor | Operational
AHU-A-F1-01~05 | Air Handling Units (x5) | AHU | Building A | Floor 1 | Same as ground floor AHUs | Same as AHU-A-GF | Chiller plant, VAVs, FCUs, DesigoCC | Loss of conditioned air — Floor 1 | Operational
AHU-A-F2-01~05 | Air Handling Units (x5) | AHU | Building A | Floor 2 | Same as ground floor AHUs | Same as AHU-A-GF | Chiller plant, VAVs, FCUs, DesigoCC | Loss of conditioned air — Floor 2. AHU 15 currently has active faults pending repair | Fault — Pending Repair
AHU-A-F3-01~05 | Air Handling Units (x5) | AHU | Building A | Floor 3 | Same as ground floor AHUs | Same as AHU-A-GF | Chiller plant, VAVs, FCUs, DesigoCC | Loss of conditioned air — Floor 3 | Operational
AHU-A-F4-01~05 | Air Handling Units (x5) | AHU | Building A | Floor 4 | Same as ground floor AHUs | Same as AHU-A-GF | Chiller plant, VAVs, FCUs, DesigoCC | Loss of conditioned air — Floor 4 | Operational
VAV-A-ALL | VAVs (multiple per floor) | VAV | Building A | All Floors | Variable air volume boxes regulate airflow to individual zones based on demand | Actuator, airflow sensor, room temperature sensor | AHUs, DesigoCC BACnet network | Loss of zone-level airflow control | Operational
FCU-A-ALL | FCUs (multiple per floor) | FCU | Building A | All Floors | Fan coil units provide localised heating/cooling to specific areas; supplement AHU supply | Fan, chilled/hot water coil, control valve, room temperature sensor | BACnet network, DesigoCC, chiller plant | Loss of localised conditioning — occupant comfort affected | Operational
DC-A-ALL | Demand Controllers | Controller | Building A | All Floors | Read feedback sensors and send commands to VAVs, FCUs, and AHUs over BACnet | MCU/PLC, BACnet interface | BACnet network, AHUs, VAVs, FCUs | Floor loses automated control — manual override required | Operational
NET-A | BACnet Network | Network | Building A | Building-wide | Independent communication backbone for all Building A assets and DesigoCC platform | Routers, cabling, network switches | All Building A assets | Full loss of automated control across Building A | Operational
DESIGO | DesigoCC Platform | SCADA | Building A | Building-wide | Central monitoring, alarm management, and control interface for Building A | Server, software, BACnet integration | All Building A assets, site engineer workstation | Loss of centralised monitoring and remote control — daily monitoring impossible | Operational
AHU-B-F1-01~05 | Air Handling Units (x5) | AHU | Building B | Floor 1 | Condition and distribute air via diffuser units; heating via two built-in heater steps | VSD fan (SAF), chilled water valve (CHWV), Heater Step 1 & 2, supply/return air temp, CHW supply/return temp, static pressure sensors | Chiller plant, diffusers, MLM controllers, Niagara | Loss of conditioned air — Building B Floor 1 | Operational
AHU-B-F2-01~05 | Air Handling Units (x5) | AHU | Building B | Floor 2 | Same as AHU-B-F1 | Same as AHU-B-F1 | Chiller plant, diffusers, MLM controllers, Niagara | Loss of conditioned air — Building B Floor 2 | Operational
AHU-B-F3-01~05 | Air Handling Units (x5) | AHU | Building B | Floor 3 | Same as AHU-B-F1 | Same as AHU-B-F1 | Chiller plant, diffusers, MLM controllers, Niagara | Loss of conditioned air — Building B Floor 3 | Operational
AHU-B-F4-01~05 | Air Handling Units (x5) | AHU | Building B | Floor 4 | Same as AHU-B-F1 | Same as AHU-B-F1 | Chiller plant, diffusers, MLM controllers, Niagara | Loss of conditioned air — Building B Floor 4 | Operational
DIFF-B-ALL | Diffuser Units (multiple per floor) | Diffuser | Building B | All Floors | Distribute conditioned air to individual rooms; each unit operates in cooling, heating, or standby mode | Temperature sensor, mode controller (cooling/heating/standby) | MLM Controllers, AHUs, Niagara BACnet | Loss of room-level temperature control | Operational
MLM-B-ALL | MLM Controllers | Controller | Building B | All Floors | Manage diffuser units and communicate AHU commands via BACnet network | MCU/PLC, BACnet interface | BACnet network, AHUs, diffusers, Rickard PSU | Entire floor loses automated diffuser control | Operational
PSU-B-ALL | Rickard PSUs | Power Supply | Building B | All Floors | Provide power to MLM controllers on each floor | PSU unit, voltage output | MLM Controllers, BACnet network | All MLM controllers on floor lose power — complete floor zone failure | Operational
NET-B | BACnet Network | Network | Building B | Building-wide | Independent communication backbone for all Building B assets and Niagara platform | Routers, cabling, network switches | All Building B assets | Full loss of automated control across Building B | Operational
NIAGARA | Niagara Tridium Platform | SCADA | Building B | Building-wide | Central monitoring, alarm management, and control interface for Building B | Server, software, BACnet integration | All Building B assets, site engineer workstation | Loss of centralised monitoring and remote control | Operational
CHILL-ROOF | Roof Chiller Plant | Chiller | Shared | Roof Level | Provides chilled water to all AHUs in both Building A and Building B | Chiller units, chilled water pumps, pipework, sensors | All AHUs in both buildings | Both buildings lose cooling capability simultaneously — highest impact shared asset | Active Alarms — Mechanical Contractor

## Risk Register (FMEA)
RISK REGISTER — FMEA ¦ Building A & Building B ¦ June 2026
Likelihood 1–5 (1=Rare, 5=Almost Certain) · Impact 1–5 (1=Negligible, 5=Catastrophic) · Score = L×I · Critical ≥15 · High 8–14 · Medium 4–7 · Low ≤3
Risk ID | Building | Asset | Failure Mode | Effect | Likelihood (1–5) | Impact (1–5) | Score (L×I) | Level | Current Controls | Recommended Action | Owner
R-01 | Shared | Roof Chiller Plant | Chiller failure or active fault | Both Building A and Building B lose cooling capability simultaneously | 3 | 5 | 15 | Critical | Life Safety alarms active; escalated to site manager | Mechanical contractor to inspect and resolve immediately; confirm backup cooling contingency | Site Manager / Mech. Contractor
R-02 | Building A | AHU 15 — Floor 2 | Multiple simultaneous controller faults (mode, heating, damper, setpoint, start command) | Floor 2 zone served by AHU 15 loses full automated HVAC control; occupant comfort affected | 5 | 4 | 20 | Critical | Faults visible on DesigoCC; being monitored | Procure and replace faulty components; prioritise approval to restore full operation | Site Automation Engineer / Building Manager
R-03 | Building A | Room Temperature — Multiple Floors | Persistent high room temperature alarms across floors 1–4 | Occupant discomfort across multiple zones; indicates systemic cooling performance issue | 5 | 3 | 15 | Critical | 282 medium alarms active and monitored on DesigoCC | Floor-by-floor inspection to identify failing equipment; prioritise procurement of parts | Site Automation Engineer / Building Manager
R-04 | Building A | Demand Controllers | Controller fault or communication loss on a floor | Entire floor loses automated VAV and FCU control; manual override required | 3 | 4 | 12 | High | DesigoCC monitors and raises alarms on fault | Confirm spare controller availability on site; document recovery procedure | Site Automation Engineer
R-05 | Building A | BACnet Network | Network communication dropout or failure | All Building A assets lose communication with DesigoCC; automated control fails across all floors | 2 | 5 | 10 | High | No redundant network path documented | Document network topology; confirm redundancy; set communication-loss alerting | Site Automation Engineer / IT
R-06 | Building B | Rickard PSU | Power supply unit failure on a floor | All MLM controllers on that floor lose power — complete Building B floor zone failure | 2 | 4 | 8 | High | Visual indicator on PSU; monitored on Niagara | Schedule quarterly PSU voltage checks; stock spare PSU on site | Site Automation Engineer
R-07 | Building B | MLM Controllers | Controller fault or communication loss | Floor loses automated diffuser and AHU command control | 3 | 3 | 9 | High | Niagara raises alarms on controller offline | Confirm spare MLM controller availability; document recovery procedure | Site Automation Engineer
R-08 | Building A | DesigoCC Platform | Platform crash, server fault, or licence issue | Loss of all centralised monitoring and alarm management for Building A; faults go undetected | 2 | 4 | 8 | High | Server monitored by IT | Confirm backup/restore procedure; verify licence renewal dates | IT / Site Automation Engineer
R-09 | Building B | AHU Heater Steps (1 & 2) | Heater step failure — one or both steps offline | Building B loses heating capability; AHU cannot meet heating demand during cold periods | 2 | 3 | 6 | Medium | Monitored on Niagara; step status visible on AHU screen | Include heater steps in periodic inspection; verify both steps activate on demand | Site Automation Engineer
R-10 | Building A | Feedback Sensors (all floors) | Sensor drift or calibration loss | Controllers receive incorrect readings; AHUs and VAVs respond incorrectly — energy waste and comfort issues | 3 | 2 | 6 | Medium | DesigoCC monitors out-of-range values | Establish annual sensor calibration schedule; log last calibration date per sensor | Site Automation Engineer
R-11 | Building B | Niagara Tridium Platform | Platform failure or network loss to Niagara supervisor | Building B loses supervisory monitoring; controllers run on last setpoint but cannot be adjusted remotely | 2 | 3 | 6 | Medium | Local controller fallback behaviour exists | Document fallback behaviour; confirm with Niagara vendor; verify backup procedure | IT / Site Automation Engineer
R-12 | Building A | AHU Filters | Filter blockage or degraded filter condition | Reduced airflow to floor; AHU fan works harder increasing energy use; air quality degrades | 3 | 2 | 6 | Medium | Filter status monitored on DesigoCC (Clean/Dirty) | Replace filters per maintenance schedule; log replacement dates | Site Automation Engineer

## Risk Summary
RISK SUMMARY DASHBOARD
Level | Count | Top Assets | Max Score | Action Timeframe | Building
Critical | 3 | Chiller, AHU 15, Room Temp Pattern | 20 | Immediate | Shared / Building A
High | 5 | BACnet, Controllers, PSU, DesigoCC | 12 | Within 30 days | Both
Medium | 4 | Sensors, Filters, Heater Steps, Niagara | 6 | Within 90 days | Both
Low | 0 | — | 3 | Monitor quarterly | —

## Maintenance Gaps
MAINTENANCE GAP ANALYSIS ¦ Building A & Building B ¦ June 2026
Asset | Building | PM Schedule Documented? | Last Inspection | Gap Identified | Recommended Action | Priority
Roof Chiller Plant | Shared | Not confirmed — active alarms present | Unknown | Life Safety alarms active; no confirmed PM schedule with mechanical contractor | Confirm PM schedule with mechanical contractor; document service history | Critical
AHU 15 — Floor 2 | Building A | Not applicable — fault condition | Unknown | Multiple simultaneous active faults; unit not operating normally | Procure parts; repair or replace faulty components; document outcome | Critical
AHU Filters — All Floors | Building A | Not confirmed | Unknown | Filter status monitored on DesigoCC but no replacement log found | Establish filter replacement schedule; log replacement dates per AHU | High
Feedback Sensors — All Floors | Building A | Not confirmed | Unknown | No sensor calibration dates documented on DesigoCC | Schedule annual calibration; create calibration log per sensor | High
AHU Heater Steps 1 & 2 | Building B | Not confirmed | Unknown | No periodic test of heater steps documented | Test both steps under load; verify activation; document results | High
Rickard PSUs — All Floors | Building B | Not confirmed | Unknown | PSU voltage output not logged regularly | Schedule quarterly voltage checks; log results; stock spare PSU on site | High
FCUs — All Floors | Building A | Not confirmed | Unknown | No FCU service or filter check schedule documented | Add FCUs to PM schedule; include coil cleaning and filter checks | Medium
MLM Controllers | Building B | Partial — Niagara alarms active | Unknown | No firmware check or physical inspection schedule documented | Confirm firmware versions; schedule annual controller health check | Medium
Demand Controllers | Building A | Partial — DesigoCC alarms active | Unknown | No firmware check or physical inspection schedule documented | Same as MLM controllers for Building A side | Medium